## Interlock Table
Inlet Work House - Interlock Table
Stage | Equipment (Start/Stop)(Open/Closed) | Internal Interlock | Interlock Status | Interlock Execution | Interlock Safety Check | Additional Interlock Concern | Auxilary Lamp | New Requirement | Function | Justification | Manual Fall Back
Sewage Stream | Stream Pump | EQ Tank Float (Dry) | [5 empty] | Yes |  | To Protect Pump Damage from Zero Water Level
|  | Stream Penstock | [7 empty] | To Protect Piping Damage and Pump Trip from pressure Build Up
|  | SBR Pump | [7 empty] | To prevent overflow due to no Feed to SBR Tank
|  | Screen Float (Overflow) | [5 empty] | Yes |  | To prevent overflow inlet House
|  | Mechanical Screen | [7 empty] | To prevent Clogging build up resulting Flood in Inlet House
Sewage Screen | Mechanical Screen | Conveyor | [7 empty] | To prevent Screened Residue over spill
|  | Screw Conveyor | [7 empty] | To prevent Screened Residue over spill
Transfer to SBR Tank | SBR Transfer Pump | [8 empty] | To Protect Piping Damage and Pump Trip from pressure Build Up
|  | Grit Removal | [7 empty] | To prevent long term Pump damage due to Hard Residue
|  | SBR Transfer Tank Float (Dry) | [5 empty] | Yes |  | To Protect Pump Damage from Zero Water Level

## PLC Assignment
Inlet Work House
A1 EK1501 #1 |  |  | A2 EL1809 #1 |  |  | A3 EL1809 #2 |  |  | A4 EL1809 #3 |  |  | A5 EL1809 #4 |  |  | A6 EL1809 #5 |  |  | A6 EL1809 #5 |  |  | A7 EL1809 #6 |  |  | A8 EL1809 #7 |  |  | A9 EL2809 #1 |  |  | A10 EL2809 #2 |  |  | A11 EL1122 #1 |  |  | A12 EL9010 #1
Coupler |  | Fiber | Digital Input Module |  | Level Sensor #S1 | Digital Input Module |  | Valve Signal #S1 Open / Close | Digital Input Module |  | Trip Signal #S1 | Digital Input Module |  | Trip Signal #S1 | Digital Input Module |  | Local / Remote #S1 | Digital Input Module |  | End Devices Status #S1 | Digital Input Module |  | Emergency Stop #S1 | Digital Input Module |  | Grit Blower S1/S2 | Digital Output Module |  | Open / Close & Start / Stop #S1 | Digital Output Module |  | Open / Close & Start / Stop #S1 | Coupler |  | E-Bus | End Terminal
|  |  | Input 1 | LSL100A | Mixer Float Sensor | Input 1 | XV101A1 | Solenoid Valve Spray 1 Open | Input 1 | M101A1 | EQ Mixer Overload 1 | Input 1 | F101A1 | Fine Screen Overload 1 | Input 1 | M101A1 | EQ Mixer 1 | Input 1 | M101A1 | EQ Mixer 1 | Input 1 | M101A1 | EQ Mixer 1 | Input 1 | B101A1 | Air Blower 1 Overload | Output 1 | XV101A1 | Water Spray Screen 1 | Output 1 | P101A1 | EQ Pump 1
|  |  | Input 2 | LSHL100A | Mixer Float Sensor | Input 2 | XV101A2 | Solenoid Valve Spray 2 Open | Input 2 | M101A1 | EQ Mixer incomplete 1 | Input 2 | F101A2 | Fine Screen Overload 2 | Input 2 | M101A2 | EQ Mixer 2 | Input 2 | M101A2 | EQ Mixer 2 | Input 2 | M101A2 | EQ Mixer 2 | Input 2 | B101A1 | AirBlower 1 Incomplete | Output 2 | XV101A2 | Water Spray Screen 2 | Output 2 | P101A2 | EQ Pump 2
|  |  | Input 3 | LSH101A | EQ Float Sensor | Input 3 | XV102A1 | Continuos Valve Water Open | Input 3 | M101A2 | EQ Mixer Overload 2 | Input 3 | C102A | Screening Conveyer Overload | Input 3 | P101A1 | EQ Pump 1 | Input 3 | P101A1 | EQ Pump 1 | Input 3 | P101A1 | EQ Pump 1 | Input 3 | B101A2 | Air Blower 2 Overload | Output 3 | XV102A1 | Continuous Spray Conveyor 1 | Output 3 | M101A1 | EQ Mixer 1
|  |  | Input 4 | LSHH101A | EQ Float Sensor | Input 4 |  |  | Input 4 | M101A2 | EQ Mixer incomplete 2 | Input 4 | C101A | Screening Compactor Overload | Input 4 | P101A2 | EQ Pump 2 | Input 4 | P101A2 | EQ Pump 2 | Input 4 | P101A2 | EQ Pump 2 | Input 4 | B101A2 | Air Blower 2 Incomplete | Output 4 | XV102A2 | Continuous Spray Conveyor 2 | Output 4 | M101A2 | EQ Mixer 2
|  |  | Input 5 | LSHL101A | EQ Float Sensor | Input 5 | XV100A1 | Grit Removal Valve 1 Open | Input 5 | P101A1 | EQ Pump Overload 1 | Input 5 | C103A | Grit Classifier Overload | Input 5 | F101A1 | Fine Screen 1 | Input 5 | F101A1 | Fine Screen 1 | Input 5 | F101A1 | Fine Screen 1 | Input 5 | B101A1 | Air Blower 1 Local / Remote | Output 5 | F101A1 | Fine Screen 1 | Output 5 | B101A1 | Grit Air Blower 1
|  |  | Input 6 | LSH105A1 | Stream Line Flow | Input 6 | XV100A2 | Grit Removal Valve 2 Open | Input 6 | P101A1 | EQ Pump Incomplete 1 | Input 6 | P102A1 | SBR Transfer Pump Overload 1 | Input 6 | F101A2 | Fine Screen 2 | Input 6 | F101A2 | Fine Screen 2 | Input 6 | F101A2 | Fine Screen 2 | Input 6 | B101A2 | Air Blower 2 Local / Remote | Output 6 | F101A2 | Fine Screen 2 | Output 6 | B101A2 | Grit Air Blower 2
|  |  | Input 7 | LSHH105A2 | Stream Line Overflow | Input 7 | PS101A1 | Motorized Penstock 1 Open | Input 7 | P101A2 | EQ Pump Overload 2 | Input 7 | P102A1 | SBR Transfer Pump Incomplete1 | Input 7 | C102A | Screen Conveyer | Input 7 | C102A | Screen Conveyer | Input 7 | C102A | Screen Conveyer | Input 7 | B101A1 | Air Blower 1 On / Off | Output 7 | C102A | Screen Conveyer | Output 7 | P102A1 | SBR Transfer Pump 1
|  |  | Input 8 | LSH103A | SBR Float Sensor | Input 8 | PS101A2 | Motorized Penstock 2 Open | Input 8 | P101A2 | EQ Pump Incomplete 2 | Input 8 | P102A2 | SBR Transfer Pump Overload 2 | Input 8 | C101A | Screen Compactor | Input 8 | C101A | Screen Compactor | Input 8 | C101A | Screen Compactor | Input 8 | B101A2 | Air Blower 2 On / Off | Output 8 | C101A | Screen Compactor | Output 8 | P102A2 | SBR Transfer Pump 2
|  |  | Input 9 | LSHH103A | SBR Float Sensor | Input 9 | PS101A1 | Motorized Penstock 1 Closed | Input 9 | PS101A1 | Motorized Penstock 1 | Input 9 | P102A2 | SBR Transfer Pump Incomplete 2 | Input 9 | C103A | Grit Clasifier | Input 9 | C103A | Grit Clasifier | Input 9 | C103A | Grit Clasifier | Input 9 | B101A1 | Air Blower 1 Emergency Stop | Output 9 | C103A | Grit Clasifier | Output 9 | AUX101A | EQ Float Sensor ALARM S1
|  |  | Input 10 | LSHL103A | SBR Float Sensor | Input 10 | PS101A2 | Motorized Penstock 2 Closed | Input 10 | PS101A2 | Motorized Penstock 2 | Input 10 |  |  | Input 10 | P102A1 | SBR Transfer Pump 1 | Input 10 | P102A1 | SBR Transfer Pump 1 | Input 10 | P102A1 | SBR Transfer Pump 1 | Input 10 | B101A2 | Air Blower 2 Emergency Stop | Output 10 | PS101A1 | Motorized Penstock 1 Open | Output 10 | AUX104A | SBR Float Sensor ALARM S1
|  |  | Input 11 | TBA | Fan Status | Input 11 | XV101A1 | Solenoid Valve Spray 1 Closed | Input 11 |  |  | Input 11 |  |  | Input 11 | P102A2 | SBR Transfer Pump 2 | Input 11 | P102A2 | SBR Transfer Pump 2 | Input 11 | P102A2 | SBR Transfer Pump 2 | Input 11 |  |  | Output 11 | PS101A1 | Motorized Penstock 1 Closed | Output 11 | AUX105A | StreamSensorOverflow S1
|  |  | Input 12 | TBA | Door Panel | Input 12 | XV101A2 | Solenoid Valve Spray 2 Closed | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Output 12 | PS101A2 | Motorized Penstock 2 Open | Output 12 | AUX107 | AUX-Common Alarm
|  |  | Input 13 | LSD101A | EQ Float Sensor DRY | Input 13 | XV102A1 | Continuos Valve Water Closed | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Output 13 | PS101A2 | Motorized Penstock 2 Closed | Output 13 | AUX108 | AUX-Power Status
|  |  | Input 14 | LSD103A | SBR Float Sensor DRY | Input 14 | XV100A1 | Grit Removal Valve 1 Closed | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Output 14 | XV100A1 | Grit Removal Suction Valve 1 | Output 14
|  |  | Input 15 |  |  | Input 15 | XV100A2 | Grit Removal Valve 2 Closed | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Output 15 | XV100A2 | Grit Removal Suction Valve 2 | Output 15
|  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Output 16 |  |  | Output 16
Legend |  |  | A13 EK1100 #1 |  |  | A14 EL1809 #8 |  |  | A15 EL1809 #9 |  |  | A16 EL1809 #10 |  |  | A17 EL1809 #11 |  |  | A18 EL1809 #12 |  |  | A19 EL1809 #13 |  |  | A20 EL1809 #14 |  |  | A21 EL1809 #15 |  |  | A22 EL1809 #16 |  |  | A23 EL2809 #3 |  |  | A24 EL2809 #4 |  |  | A25 EL9010 #2
| Coupler |  | Coupler |  | E-Bus | Digital Input Module |  | Level Sensor #S2 | Digital Input Module |  | Valve Signal #S2 Open / Close Status | Digital Input Module |  | Trip Signal #S2 | Digital Input Module |  | Trip Signal #S2 | Digital Input Module |  | Local / Remote #2 | Digital Input Module |  | End Devices Status #2 | Digital Input Module |  | Emergency Stop #2 | Digital Input Module |  | Odour | Digital Input Module |  | Odour | Digital Output Module |  | Open / Close & Start / Stop #2 | Digital Output Module |  | Open / Close & Start / Stop #2 | End Terminal
| Input |  |  |  |  | Input 1 | LSL100B | Mixer Float Sensor | Input 1 | XV101B1 | Solenoid Valve Spray 1 Open | Input 1 | M101B1 | EQ Mixer Overload 1 | Input 1 | F101B1 | Fine Screen Overload 1 | Input 1 | M101B1 | EQ Mixer 1 | Input 1 | M101B1 | EQ Mixer 1 | Input 1 | M101B1 | EQ Mixer 1 | Input 1 | VE801A | Suction Fan On / Off | Input 1 | P806A1 | NAOH Pump 1 Overload | Output 1 | XV101B1 | Water Spray Screen 1 | Output 1 | P101B1 | EQ Pump 1
| Output |  |  |  |  | Input 2 | LSHL100B | Mixer Float Sensor | Input 2 | XV101B2 | Solenoid Valve Spray 2 Open | Input 2 | M101B1 | EQ Mixer incomplete 1 | Input 2 | F101B2 | Fine Screen Overload 2 | Input 2 | M101B2 | EQ Mixer 2 | Input 2 | M101B2 | EQ Mixer 2 | Input 2 | M101B2 | EQ Mixer 2 | Input 2 | P802A | Circulation Pump 1 On / Off | Input 2 | P806A2 | NAOH Pump 2 Overload | Output 2 | XV101B2 | Water Spray Screen 2 | Output 2 | P101B2 | EQ Pump 2
| Analog |  |  |  |  | Input 3 | LSH101B | EQ Float Sensor | Input 3 | XV102B1 | Continuos Valve Water Open | Input 3 | M101B2 | EQ Mixer Overload 2 | Input 3 | C102B | Screening Conveyer Overload | Input 3 | P101B1 | EQ Pump 1 | Input 3 | P101B1 | EQ Pump 1 | Input 3 | P101B1 | EQ Pump 1 | Input 3 | P803A | Circulation Pump 2 On / Off | Input 3 | P807A1 | NAOCL Pump 1 Overload | Output 3 | XV102B1 | Continuous Spray Conveyor 1 | Output 3 | M101B1 | EQ Mixer 1
| End Terminal |  |  |  |  | Input 4 | LSHH101B | EQ Float Sensor | Input 4 |  |  | Input 4 | M101B2 | EQ Mixer incomplete 2 | Input 4 | C101B | Screening Compactor Overload | Input 4 | P101B2 | EQ Pump 2 | Input 4 | P101B2 | EQ Pump 2 | Input 4 | P101B2 | EQ Pump 2 | Input 4 | P804A | Circulation Pump 3 On / Off | Input 4 | P807A2 | NAOCL Pump 2 Overload | Output 4 | XV102B2 | Continuous Spray Conveyor 2 | Output 4 | M101B2 | EQ Mixer 2
[6 empty] | Input 5 | LSHL101B | EQ Float Sensor | Input 5 | XV100B1 | Grit Removal Valve 1 Open | Input 5 | P101B1 | EQ Pump Overload 1 | Input 5 | C103B | Grit Classifier Overload | Input 5 | F101B1 | Fine Screen 1 | Input 5 | F101B1 | Fine Screen 1 | Input 5 | F101B1 | Fine Screen 1 | Input 5 | P805A1 | H2S04 Pump 1 On / Off | Input 5 | VE801A | Suction Fan E-Stop | Output 5 | F101B1 | Fine Screen 1 | Output 5 | P102B1 | SBR Transfer Pump 1
[6 empty] | Input 6 | LSH10HB1 | Stream Line Flow | Input 6 | XV100B2 | Grit Removal Valve 2 Open | Input 6 | P101B1 | EQ Pump Incomplete 1 | Input 6 | P102B1 | SBR Transfer Pump Overload 1 | Input 6 | F101B2 | Fine Screen 2 | Input 6 | F101B2 | Fine Screen 2 | Input 6 | F101B2 | Fine Screen 2 | Input 6 | P805A2 | H2S04 Pump 2 On / Off | Input 6 | P802A | Circulation Pump 1 E-Stop | Output 6 | F101B2 | Fine Screen 2 | Output 6 | P102B2 | SBR Transfer Pump 2
[6 empty] | Input 7 | LSHH105B2 | Stream Line Overflow | Input 7 | PS101B1 | Motorized Penstock 1 Open | Input 7 | P101B2 | EQ Pump Overload 2 | Input 7 | P102B1 | SBR Transfer Pump Incomplete1 | Input 7 | C102B | Screen Conveyer | Input 7 | C102B | Screen Conveyer | Input 7 | C102B | Screen Conveyer | Input 7 | P806A1 | NAOH Pump 1 On / Off | Input 7 | P803A | Circulation Pump 2 E-Stop | Output 7 | C102B | Screen Conveyer | Output 7 | AUX101B | EQ Float Sensor ALARM S2
[6 empty] | Input 8 | LSH103B | SBR Float Sensor | Input 8 | PS101B2 | Motorized Penstock 2 Open | Input 8 | P101B2 | EQ Pump Incomplete 2 | Input 8 | P102B2 | SBR Transfer Pump Overload 2 | Input 8 | C101B | Screen Compactor | Input 8 | C101B | Screen Compactor | Input 8 | C101B | Screen Compactor | Input 8 | P806A2 | NAOH Pump 2 On / Off | Input 8 | P804A | Circulation Pump 3 E-Stop | Output 8 | C101B | Screen Compactor | Output 8 | AUX104B | SBR Float Sensor ALARM S2
[6 empty] | Input 9 | LSHH103B | SBR Float Sensor | Input 9 | PS101B1 | Motorized Penstock 1 Closed | Input 9 | PS101B1 | Motorized Penstock 1 | Input 9 | P102B2 | SBR Transfer Pump Incomplete 2 | Input 9 | C103B | Grit Clasifier | Input 9 | C103B | Grit Clasifier | Input 9 | C103B | Grit Clasifier | Input 9 | P807A1 | NAOCL Pump 1 On / Off | Input 9 | P805A1 | H2S04 Pump 1 E-Stop | Output 9 | C103B | Grit Clasifier | Output 9 | AUX105B | StreamSensorOverflow S2
[6 empty] | Input 10 | LSHL103B | SBR Float Sensor | Input 10 | PS101B2 | Motorized Penstock 2 Closed | Input 10 | PS101B2 | Motorized Penstock 2 | Input 10 |  |  | Input 10 | P102B1 | SBR Transfer Pump 1 | Input 10 | P102B1 | SBR Transfer Pump 1 | Input 10 | P102B1 | SBR Transfer Pump 1 | Input 10 | P807A2 | NAOCL Pump 2 On / Off | Input 10 | P805A2 | H2S04 Pump 2 E-Stop | Output 10 | PS101B1 | Motorized Penstock 1 Open | Output 10
[6 empty] | Input 11 | LSD101B | EQ Float Sensor DRY | Input 11 | XV101B1 | Solenoid Valve Spray 1 Closed | Input 11 |  |  | Input 11 |  |  | Input 11 | P102B2 | SBR Transfer Pump 2 | Input 11 | P102B2 | SBR Transfer Pump 2 | Input 11 | P102B2 | SBR Transfer Pump 2 | Input 11 | VE801A | Suction Fan Overload | Input 11 | P806A1 | NAOH Pump 1 E-Stop | Output 11 | PS101B1 | Motorized Penstock 1 Closed | Output 11
[6 empty] | Input 12 | LSD103B | SBR Float Sensor DRY | Input 12 | XV101B2 | Solenoid Valve Spray 2 Closed | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 |  |  | Input 12 | P802A | Circulation Pump 1 Overload | Input 12 | P806A2 | NAOH Pump 2 E-Stop | Output 12 | PS101B2 | Motorized Penstock 2 Open | Output 12
[6 empty] | Input 13 |  |  | Input 13 | XV102B1 | Continuos Valve Water Closed | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 |  |  | Input 13 | P803A | Circulation Pump 2 Overload | Input 13 | P807A1 | NAOCL Pump 1 E-Stop | Output 13 | PS101B2 | Motorized Penstock 2 Closed | Output 13
[6 empty] | Input 14 |  |  | Input 14 | XV100B1 | Grit Removal Valve 1 Closed | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 |  |  | Input 14 | P804A | Circulation Pump 3 Overload | Input 14 | P807A2 | NAOCL Pump 2 E-Stop | Output 14 | XV100B1 | Grit Removal Suction Valve 1 | Output 14
[6 empty] | Input 15 |  |  | Input 15 | XV100B2 | Grit Removal Valve 2 Closed | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 | P805A1 | H2S04 Pump 1 Overload | Input 15 |  |  | Output 15 | XV100B2 | Grit Removal Suction Valve 2 | Output 15
[6 empty] | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 | P805A2 | H2S04 Pump 2 Overload | Input 16 |  |  | Output 16 |  |  | Output 16