## Interlock Table
Blower System - Interlock Table
Stage | Equipment (Start/Stop)(Open/Closed) | Internal Interlock | Interlock Status | Interlock Execution | Interlock Safety Check | Additional Interlock Concern | Auxilary Lamp | New Requirement | Function | Justification | Manual Fall Back
Filling | Filling Valve (OPEN) | Mixer (STOP) | [6 empty] | Evenly Distribute sewage for equalibrium reaction in Tank | Early Startup - Wasted Run Hour
|  | SBR Pump (START) | [7 empty] | To Fill SBR Tank
|  | Decanter (UP) | [6 empty] | Discharge Water | To prevent unprocessed sewage to exit tank prematurely
|  | Sludge Pump (STOP) | [7 empty] | To prevent unprocessed sludge to exit tank prematurely
|  | Blower (STOP) | [7 empty] | Early Startup - Wasted Run Hour
|  | SBR Tank Float (Operation) | [6 empty] | To trigger End of filling Process and Start of Aeration | Signals Optimum Sewage operation Level
Reactor Operation Button
Aeration
Settle
Decant

## PLC Assignment
Secondary Treatment (Blower House S#1 and S#2)
A1 EK1100 #1 |  |  | A2 EL1809 #1 |  |  | A3 EL1809 #2 |  |  | A4 EL1809 #3 |  |  | A5 EL1809 #4 |  |  | A6 EL1809 #5 |  |  | A7 EL1809 #6 |  |  | A8 EL1809 #7 |  |  | A9 EL1809 #8 |  |  | A9 EL1809 #9 |  |  | A10 EL3054 #1 |  |  | A11 EL2809 #1 |  |  | A12 EL2809 #2 |  |  | A13 EL2809 #3 |  |  | A14 EL9011 #1
Coupler |  | E-Bus | Digital Input Module |  | Status #S1 | Digital Input Module |  | Open / Close & Start / Stop Status #S1 | Digital Input Module |  | Local / Remote | Digital Input Module |  | Local / Remote | Digital Input Module |  | Trip Signal | Digital Input Module |  | Trip Signal | Digital Input Module |  | Emergency Stop #S1 | Digital Input Module |  | Emergency Stop #S1 | Digital Input Module |  | Emergency Stop #S1 | Analog Input Module |  | Sensor | Digital Output Module |  | Open / Close & Start / Stop #S1 | Digital Output Module |  | Open / Close & Start / Stop #S1 | Digital Output Module |  | AUXILARY ALARM | End Terminal
|  |  | Input 1 | TBA | Fan Status | Input 1 | M200A1A | Mixer 1 #R1 | Input 1 | M200A1A | Mixer 1 #R1 | Input 1 | B201A1 | Air Blower 1 #S1 | Input 1 | M200A1A | Mixer 1 #R1 Overload | Input 1 | M200A3C | Mixer 3 #R3 Overload | Input 1 | M200A1A | Mixer 1 #R1 | Input 1 | B201A1 | Air Blower 1 #S1 | Input 1 | XV261A | Decanter #R1 Forward | Input 1 | FT100A | Flow Totalizer #S1 | Output 1 | M200A1A | Mixer 1 #R1 | Output 1 | XV261A | Decanter Forward #R1 | Output 1 | AUX -A1 | Reactor Operation 1-1
|  |  | Input 2 | TBA | Door Panel | Input 2 | M200A1B | Mixer 2 #R1 | Input 2 | M200A1B | Mixer 2 #R1 | Input 2 | B201A2 | Air Blower 2 #S1 | Input 2 |  | Mixer 1 #R1 Incomplete | Input 2 |  | Mixer 3 #R3 Incomplete | Input 2 | M200A1B | Mixer 2 #R1 | Input 2 | B201A2 | Air Blower 2 #S1 | Input 2 | XV262A | Decanter #R2 Forward | Input 2 |  |  | Output 2 | M200A1B | Mixer 2 #R1 | Output 2 | XV262A | Decanter Forward #R2 | Output 2 | AUX -A2 | Reactor Operation 1-2
|  |  | Input 3 | XV261A | Decanter #R1 Overload | Input 3 | M200A1C | Mixer 3 #R1 | Input 3 | M200A1C | Mixer 3 #R1 | Input 3 | B201A3 | Air Blower 3 #S1 | Input 3 | M200A1B | Mixer 2 #R1 Overload | Input 3 | M200A4A | Mixer 1 #R4 Overload | Input 3 | M200A1C | Mixer 3 #R1 | Input 3 | B201A3 | Air Blower 3 #S1 | Input 3 | XV263A | Decanter #R3 Forward | Input 3 |  |  | Output 3 | M200A1C | Mixer 3 #R1 | Output 3 | XV263A | Decanter Forward #R3 | Output 3 | AUX -A3 | Reactor Operation 1-3
|  |  | Input 4 | XV262A | Decanter #R2 Overload | Input 4 | M200A2A | Mixer 1 #R2 | Input 4 | M200A2A | Mixer 1 #R2 | Input 4 | XV261A | Decanter #R1 | Input 4 |  | Mixer 2 #R1 Incomplete | Input 4 |  | Mixer 1 #R4 Incomplete | Input 4 | M200A2A | Mixer 1 #R2 | Input 4 | XV261B | Decanter #R1 | Input 4 | XV264A | Decanter #R4 Forward | Input 4 |  |  | Output 4 | M200A2A | Mixer 1 #R2 | Output 4 | XV264A | Decanter Forward #R4 | Output 4 | AUX -A4 | Reactor Operation 1-4
|  |  | Input 5 | XV263A | Decanter #R3 Overload | Input 5 | M200A2B | Mixer 2 #R2 | Input 5 | M200A2B | Mixer 2 #R2 | Input 5 | XV262A | Decanter #R2 | Input 5 | M200A1C | Mixer 3 #R1 Overload | Input 5 | M200A4B | Mixer 2 #R4 Overload | Input 5 | M200A2B | Mixer 2 #R2 | Input 5 | XV262B | Decanter #R2 | Input 5 | XV261A | Decanter #R1 Reverse |  |  |  | Output 5 | M200A2B | Mixer 2 #R2 | Output 5 | XV261A | Decanter Reverse #R1 | Output 5 | AUX -B1 | Reactor Operation 2-1
|  |  | Input 6 | XV264A | Decanter #R4 Overload | Input 6 | M200A2C | Mixer 3 #R2 | Input 6 | M200A2C | Mixer 3 #R2 | Input 6 | XV263A | Decanter #R3 | Input 6 |  | Mixer 3 #R1 Incomplete | Input 6 |  | Mixer 2 #R4 Incomplete | Input 6 | M200A2C | Mixer 3 #R2 | Input 6 | XV263B | Decanter #R3 | Input 6 | XV262A | Decanter #R2 Reverse |  |  |  | Output 6 | M200A2C | Mixer 3 #R2 | Output 6 | XV262A | Decanter Reverse #R2 | Output 6 | AUX -B2 | Reactor Operation 2-2
|  |  | Input 7 |  |  | Input 7 | M200A3A | Mixer 1 #R3 | Input 7 | M200A3A | Mixer 1 #R3 | Input 7 | XV264A | Decanter #R4 | Input 7 | M200A2A | Mixer 1 #R2 Overload | Input 7 | M200A4C | Mixer 3 #R4 Overload | Input 7 | M200A3A | Mixer 1 #R3 | Input 7 | XV264B | Decanter #R4 | Input 7 | XV263A | Decanter #R3 Reverse |  |  |  | Output 7 | M200A3A | Mixer 1 #R3 | Output 7 | XV263A | Decanter Reverse #R3 | Output 7 | AUX -B3 | Reactor Operation 2-3
|  |  | Input 8 |  |  | Input 8 | M200A3B | Mixer 2 #R3 | Input 8 | M200A3B | Mixer 2 #R3 | Input 8 | P201A1 | Desludge Pump 1 #S1 | Input 8 |  | Mixer 1 #R2 Incomplete | Input 8 |  | Mixer 3 #R4 Incomplete | Input 8 | M200A3B | Mixer 2 #R3 | Input 8 | P201A1 | Desludge Pump 1 #S1 | Input 8 | XV264A | Decanter #R4 Reverse |  |  |  | Output 8 | M200A3B | Mixer 2 #R3 | Output 8 | XV264A | Decanter Reverse #R4 | Output 8 | AUX -B4 | Reactor Operation 2-4
|  |  | Input 9 |  |  | Input 9 | M200A3C | Mixer 3 #R3 | Input 9 | M200A3C | Mixer 3 #R3 | Input 9 | P201A2 | Desludge Pump 2 #S1 | Input 9 | M200A2B | Mixer 2 #R2 Overload | Input 9 | B201A1 | Air Blower 1 #S1 Overload | Input 9 | M200A3C | Mixer 3 #R3 | Input 9 | P201A2 | Desludge Pump 2 #S1 | Input 9 | [5 empty] | Output 9 | M200A3C | Mixer 3 #R3 | Output 9 | B201A1 | Air Blower 1 #S1 | Output 9 | AUX -A5 | Blower S1-1
|  |  | Input 10 |  |  | Input 10 | M200A4A | Mixer 1 #R4 | Input 10 | M200A4A | Mixer 1 #R4 | Input 10 | P201A1 | Desludge Pump 1 Start#S1 |  |  | Mixer 2 #R2 Incomplete | Input 10 |  | Air Blower 1 #S1 Incomplete | Input 10 | M200A4A | Mixer 1 #R4 | Input 10 |  |  | Input 10 | [5 empty] | Output 10 | M200A4A | Mixer 1 #R4 | Output 10 | B201A2 | Air Blower 2 #S1 | Output 10 | AUX -A6 | Blower S1-2
|  |  | Input 11 |  |  | Input 11 | M200A4B | Mixer 2 #R4 | Input 11 | M200A4B | Mixer 2 #R4 | Input 11 | P201A2 | Desludge Pump 2 Start#S1 |  | M200A2C | Mixer 3 #R2 Overload | Input 11 | B201A2 | Air Blower 2 #S1 Overload | Input 11 | M200A4B | Mixer 2 #R4 | Input 11 |  |  | Input 11 | [5 empty] | Output 11 | M200A4B | Mixer 2 #R4 | Output 11 | B201A3 | Air Blower 3 #S1 | Output 11 | AUX -A7 | Blower S1-3
|  |  | Input 12 |  |  | Input 12 | M200A4C | Mixer 3 #R4 | Input 12 | M200A4C | Mixer 3 #R4 | Input 12 |  |  | Input 12 |  | Mixer 3 #R2 Incomplete | Input 12 |  | Air Blower 2 #S1 Incomplete | Input 12 | M200A4C | Mixer 3 #R4 | Input 12 |  |  | Input 12 | [5 empty] | Output 12 | M200A4C | Mixer 3 #R4 | Output 12 | P201A1 | Desludge Pump 1 #S1 | Output 12 | AUX -B5 | Blower S2-1
|  |  | Input 13 |  |  | Input 13 | B201A1 | Air Blower 1 #S1 | Input 13 |  |  | Input 13 |  |  | Input 13 | M200A3A | Mixer 1 #R3 Overload | Input 13 | B201A3 | Air Blower 3 #S1 Overload | Input 13 |  |  | Input 13 |  |  | Input 13 | [5 empty] | Output 13 |  |  | Output 13 | P201A2 | Desludge Pump 2 #S1 | Output 13 | AUX -B6 | Blower S2-2
|  |  | Input 14 |  |  | Input 14 | B201A2 | Air Blower 2 #S1 | Input 14 |  |  | Input 14 |  |  | Input 14 |  | Mixer 1 #R3 Incomplete | Input 14 |  | Air Blower 3 #S1 Incomplete | Input 14 |  |  | Input 14 |  |  | Input 14 | [5 empty] | Output 14 |  |  | Output 14 |  |  | Output 14 | AUX -B7 | Blower S2-3
|  |  | Input 15 |  |  | Input 15 | B201A3 | Air Blower 3 #S1 | Input 15 |  |  | Input 15 |  |  | Input 15 | M200A3B | Mixer 2 #R3 Overload | Input 15 | P201A1 | Desludge Pump 1 #S1 Overload | Input 15 |  |  | Input 15 |  |  | Input 15 | [5 empty] | Output 15 |  |  | Output 15 |  |  | Output 15 | AUX -Alarm1 | AUX-Alarm Event
|  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  | Mixer 2 #R3 Incomplete | Input 16 | P201A2 | Desludge Pump 2 #S1 Overload | Input 16 |  |  | Input 16 |  |  | Input 16 | [5 empty] | Output 16 |  |  | Output 16 |  |  | Output 16 | AUX-PWR | AUX-Power Status
|  |  | A15 EK1501 #1 |  |  | A16 EL1809 #10 |  |  | A17 EL1809 #11 |  |  | A18 EL1809 #12 |  |  | A19 EL1809 #13 |  |  | A20 EL1809 #14 |  |  | A21 EL1809 #15 |  |  | A22 EL1809 #16 |  |  | A23 EL1809 #17 |  |  | A24 EL1809 #18 |  |  | A25 EL3054 #2 |  |  | A26 EL2809 #4 |  |  | A27 EL2809 #5 |  |  | A28 EL1122 #1 |  | A29 EL9011 #2
Legend |  |  | Coupler |  | Fiber | Digital Input Module |  | Status #S2 | Digital Input Module |  | Open / Close & Start / Stop Status #S2 | Digital Input Module |  | Local / Remote | Digital Input Module |  | Local / Remote | Digital Input Module |  | Trip Signal | Digital Input Module |  | Trip Signal | Digital Input Module |  | Emergency Stop #S1 | Digital Input Module |  | Emergency Stop #S1 | Digital Input Module |  | Emergency Stop #S1 | Analog Input Module |  | Sensor | Digital Output Module |  | Open / Close & Start / Stop #S1 | Digital Output Module |  | Open / Close & Start / Stop #S1 | Coupler | E-Bus | End Terminal
| Coupler |  |  |  |  | Input 1 | TBA | Fan Status | Input 1 | M200B1A | Mixer 1 #R1 | Input 1 | M200B1A | Mixer 1 #R1 | Input 1 | B201B1 | Air Blower 1 #S1 | Input 1 | M200B1A | Mixer 1 #R1 Overload | Input 1 | M200B3C | Mixer 3 #R3 Overload | Input 1 | M200B1A | Mixer 1 #R1 | Input 1 | B201B1 | Air Blower 1 #S1 | Input 1 | XV261B | Decanter #R1 Forward | Input 1 | FT100B | Flow Totalizer #S2 | Output 1 | M200B1A | Mixer 1 #R1 | Output 1 | XV261B | Decanter Forward #R1
| Input |  |  |  |  | Input 2 | TBA | Door Panel | Input 2 | M200B1B | Mixer 2 #R1 | Input 2 | M200B1B | Mixer 2 #R1 | Input 2 | B201B2 | Air Blower 2 #S1 | Input 2 |  | Mixer 1 #R1 Incomplete | Input 2 |  | Mixer 3 #R3 Incomplete | Input 2 | M200B1B | Mixer 2 #R1 | Input 2 | B201B2 | Air Blower 2 #S1 | Input 2 | XV262B | Decanter #R2 Forward | Input 2 |  |  | Output 2 | M200B1B | Mixer 2 #R1 | Output 2 | XV262B | Decanter Forward #R2
| Output |  |  |  |  | Input 3 | XV261B | Decanter #R1 Overload | Input 3 | M200B1C | Mixer 3 #R1 | Input 3 | M200B1C | Mixer 3 #R1 | Input 3 | B201B3 | Air Blower 3 #S1 | Input 3 | M200B1B | Mixer 2 #R1 Overload | Input 3 | M200B4A | Mixer 1 #R4 Overload | Input 3 | M200B1C | Mixer 3 #R1 | Input 3 | B201B3 | Air Blower 3 #S1 | Input 3 | XV263B | Decanter #R3 Forward | Input 3 |  |  | Output 3 | M200B1C | Mixer 3 #R1 | Output 3 | XV263B | Decanter Forward #R3
| Analog |  |  |  |  | Input 4 | XV262B | Decanter #R2 Overload | Input 4 | M200B2A | Mixer 1 #R2 | Input 4 | M200B2A | Mixer 1 #R2 | Input 4 | XV261B | Decanter #R1 | Input 4 |  | Mixer 2 #R1 Incomplete | Input 4 |  | Mixer 1 #R4 Incomplete | Input 4 | M200B2A | Mixer 1 #R2 | Input 4 | XV261B | Decanter #R1 | Input 4 | XV264B | Decanter #R4 Forward | Input 4 |  |  | Output 4 | M200B2A | Mixer 1 #R2 | Output 4 | XV264B | Decanter Forward #R4
| End Terminal |  |  |  |  | Input 5 | XV263B | Decanter #R3 Overload | Input 5 | M200B2B | Mixer 2 #R2 | Input 5 | M200B2B | Mixer 2 #R2 | Input 5 | XV262B | Decanter #R2 | Input 5 | M200B1C | Mixer 3 #R1 Overload | Input 5 | M200B4B | Mixer 2 #R4 Overload | Input 5 | M200B2B | Mixer 2 #R2 | Input 5 | XV262B | Decanter #R2 | Input 5 | XV261B | Decanter #R1 Reverse |  |  |  | Output 5 | M200B2B | Mixer 2 #R2 | Output 5 | XV261B | Decanter Reverse #R1
[6 empty] | Input 6 | XV264B | Decanter #R4 Overload | Input 6 | M200B2C | Mixer 3 #R2 | Input 6 | M200B2C | Mixer 3 #R2 | Input 6 | XV263B | Decanter #R3 | Input 6 |  | Mixer 3 #R1 Incomplete | Input 6 |  | Mixer 2 #R4 Incomplete | Input 6 | M200B2C | Mixer 3 #R2 | Input 6 | XV263B | Decanter #R3 | Input 6 | XV262B | Decanter #R2 Reverse |  |  |  | Output 6 | M200B2C | Mixer 3 #R2 | Output 6 | XV262B | Decanter Reverse #R2
[6 empty] | Input 7 |  |  | Input 7 | M200B3A | Mixer 1 #R3 | Input 7 | M200B3A | Mixer 1 #R3 | Input 7 | XV264B | Decanter #R4 | Input 7 | M200B2A | Mixer 1 #R2 Overload | Input 7 | M200B4C | Mixer 3 #R4 Overload | Input 7 | M200B3A | Mixer 1 #R3 | Input 7 | XV264B | Decanter #R4 | Input 7 | XV263B | Decanter #R3 Reverse |  |  |  | Output 7 | M200B3A | Mixer 1 #R3 | Output 7 | XV263B | Decanter Reverse #R3
[6 empty] | Input 8 |  |  | Input 8 | M200B3B | Mixer 2 #R3 | Input 8 | M200B3B | Mixer 2 #R3 | Input 8 | P201B1 | Desludge Pump 1 #S1 | Input 8 |  | Mixer 1 #R2 Incomplete | Input 8 |  | Mixer 3 #R4 Incomplete | Input 8 | M200B3B | Mixer 2 #R3 | Input 8 | P201B1 | Desludge Pump 1 #S1 | Input 8 | XV264B | Decanter #R4 Reverse |  |  |  | Output 8 | M200B3B | Mixer 2 #R3 | Output 8 | XV264B | Decanter Reverse #R4
[6 empty] | Input 9 |  |  | Input 9 | M200B3C | Mixer 3 #R3 | Input 9 | M200B3C | Mixer 3 #R3 | Input 9 | P201B2 | Desludge Pump 2 #S1 | Input 9 | M200B2B | Mixer 2 #R2 Overload | Input 9 | B201B1 | Air Blower 1 #S1 Overload | Input 9 | M200B3C | Mixer 3 #R3 | Input 9 | P201B2 | Desludge Pump 2 #S1 | Input 9 | [5 empty] | Output 9 | M200B3C | Mixer 3 #R3 | Output 9 | B201B1 | Air Blower 1 #S2
[6 empty] | Input 10 |  |  | Input 10 | M200B4A | Mixer 1 #R4 | Input 10 | M200B4A | Mixer 1 #R4 | Input 10 | P201B1 | Desludge Pump 1 Start #S2 |  |  | Mixer 2 #R2 Incomplete | Input 10 |  | Air Blower 1 #S1 Incomplete | Input 10 | M200B4A | Mixer 1 #R4 | Input 10 |  |  | Input 10 | [5 empty] | Output 10 | M200B4A | Mixer 1 #R4 | Output 10 | B201B2 | Air Blower 2 #S2
[6 empty] | Input 11 |  |  | Input 11 | M200B4B | Mixer 2 #R4 | Input 11 | M200B4B | Mixer 2 #R4 | Input 11 | P201B2 | Desludge Pump 2 Start #S2 |  | M200B2C | Mixer 3 #R2 Overload | Input 11 | B201B2 | Air Blower 2 #S1 Overload | Input 11 | M200B4B | Mixer 2 #R4 | Input 11 |  |  | Input 11 | [5 empty] | Output 11 | M200B4B | Mixer 2 #R4 | Output 11 | B201B3 | Air Blower 3 #S2
[6 empty] | Input 12 |  |  | Input 12 | M200B4C | Mixer 3 #R4 | Input 12 | M200B4C | Mixer 3 #R4 | Input 12 |  |  | Input 12 |  | Mixer 3 #R2 Incomplete | Input 12 |  | Air Blower 2 #S1 Incomplete | Input 12 | M200B4C | Mixer 3 #R4 | Input 12 |  |  | Input 12 | [5 empty] | Output 12 | M200B4C | Mixer 3 #R4 | Output 12 | P201B1 | Desludge Pump 1 #S2
[6 empty] | Input 13 |  |  | Input 13 | B201B1 | Air Blower 1 #S2 | Input 13 |  |  | Input 13 |  |  | Input 13 | M200B3A | Mixer 1 #R3 Overload | Input 13 | B201B3 | Air Blower 3 #S1 Overload | Input 13 |  |  | Input 13 |  |  | Input 13 | [5 empty] | Output 13 |  |  | Output 13 | P201B2 | Desludge Pump 2 #S2
[6 empty] | Input 14 |  |  | Input 14 | B201B2 | Air Blower 2 #S2 | Input 14 |  |  | Input 14 |  |  | Input 14 |  | Mixer 1 #R3 Incomplete | Input 14 |  | Air Blower 3 #S1 Incomplete | Input 14 |  |  | Input 14 |  |  | Input 14 | [5 empty] | Output 14 |  |  | Output 14
[6 empty] | Input 15 |  |  | Input 15 | B201B3 | Air Blower 3 #S2 | Input 15 |  |  | Input 15 |  |  | Input 15 | M200B3B | Mixer 2 #R3 Overload | Input 15 | P201B1 | Desludge Pump 1 #S1 Overload | Input 15 |  |  | Input 15 |  |  | Input 15 | [5 empty] | Output 15 |  |  | Output 15
[6 empty] | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  | Mixer 2 #R3 Incomplete | Input 16 | P201B2 | Desludge Pump 2 #S1 Overload | Input 16 |  |  | Input 16 |  |  | Input 16 | [5 empty] | Output 16 |  |  | Output 16