## Interlock Table
Chemical Dosing and Tertiary Plant Treantment- Interlock Table
Stage | Equipment (Start/Stop)(Open/Closed) | Internal Interlock | Interlock Status | Interlock Execution | Interlock Safety Check | Additional Interlock Concern | Auxilary Lamp | New Requirement | Function | Justification | Manual Fall Back

## PLC Assignment
Tertiary Treatment (Chemical Dosing & Effluent Polish)
A1 EK1501 #1 |  |  | A3 EL1809 #1 |  |  | A4 EL1809 #2 |  |  | A5 EL1809 #3 |  |  | A6 EL1809 #4 |  |  | A7 EL1809 #5 |  |  | A8 EL1809 #6 |  |  | A9 EL1809 #7 |  |  | A10 EL1309 #8 |  |  | A11 EL1309 #9 |  |  | A12 EL1309 #10 |  |  | A13 EL1309 #11 |  |  | A14 EL1309 #12 |  |  | A15 EL1309 #13 |  |  | A16 EL1122 #1 |  | A17 EL9011 #1
Coupler |  | Fiber | Digital Input Module |  | Level Sensor | Digital Input Module |  | Level Sensor | Digital Input Module |  | STATUS | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Local /Remote Status | Digital Input Module |  | Local /Remote Status | Digital Input Module |  | Trip Signal | Digital Input Module |  | Trip Signal | Digital Input Module |  | Emergency Stop | Digital Input Module |  | Emergency Stop | Coupler | E-Bus | End Terminal
|  |  | Input 1 | LSHH210A | Lime Tank 1 (T210A) | Input 1 | LSL355A | Sodium Hypochlorite Tank 1 (T355A) | Input 1 | XV251A | Lime Selector Tank 1 (T210A) Open | Input 1 | P210A1 | Lime Pump 1 #S1 | Input 1 | P354A | Caustic Soda Pump 1 | Input 1 | TBA | Fan Status | Input 1 | XV303A | Lamella 1 Sludge Discharge (T303A) Closed | Input 1 | P210A1 | Lime Pump 1 #S1 | Input 1 | P204A | Sodium Hypochlorite Pump 1 Disinfection Tank | Input 1 | P210A1 | Lime Pump 1 #S1 | Input 1 | P204A | Sodium Hypochlorite Pump 1 Disinfection Tank | Input 1 | P210A1 | Lime Pump 1 #S1 | Input 1 | P204A | Sodium Hypochlorite Pump 1 Disinfection Tank
|  |  | Input 2 | LSH210A | Lime Tank 1 (T210A) | Input 2 | LSL355B | Sodium Hypochlorite Tank 2 (T355B) | Input 2 | XV251B | Lime Selector Tank 2 (T210B) Open | Input 2 | P210A2 | Lime Pump 2 #S1/S2 | Input 2 | P354B | Caustic Soda Pump 2 | Input 2 | TBA | Door Panel | Input 2 | XV303B | Lamella 2 Sludge Discharge (T303B) Closed | Input 2 | P210A2 | Lime Pump 2 #S1 | Input 2 | P204B | Sodium Hypochlorite Pump 2 Disinfection Tank | Input 2 | P210A2 | Lime Pump 2 #S1 | Input 2 | P204B | Sodium Hypochlorite Pump 2 Disinfection Tank | Input 2 | P210A2 | Lime Pump 2 #S1 | Input 2 | P204B | Sodium Hypochlorite Pump 2 Disinfection Tank
|  |  | Input 3 | LSL210A | Lime Tank 1 (T210A) | Input 3 | LSL355C | Sodium Hypochlorite Tank 3 (T355C) | Input 3 | XV251C | Lime Selector Tank 3 (T210C) Open | Input 3 | P210A3 | Lime Pump 3 #S2 | Input 3 | P356A | Sodium Hypochlorite Pump 1 Chlorine tank | Input 3 | XV250A | Lime Water Intake Tank 1 (T210A) Open | Input 3 | XV303C | Lamella 3 Sludge Discharge (T303C) Closed | Input 3 | P210A3 | Lime Pump 3 #S1 | Input 3 | P356A | Sodium Hypochlorite Pump 1 Chlorine tank | Input 3 | P210A3 | Lime Pump 3 #S1 | Input 3 | P356A | Sodium Hypochlorite Pump 1 Chlorine tank | Input 3 | P210A3 | Lime Pump 3 #S1 | Input 3 | P356A | Sodium Hypochlorite Pump 1 Chlorine tank
|  |  | Input 4 | LSLL210A | Lime Tank 1 (T210A) | Input 4 | LS353A | Caustic Soda Tank 1 (T353A) | Input 4 | XV251A | Lime Selector Tank 1 (T210A) C losed | Input 4 | P203A | Lime Circulation Pump 1 | Input 4 | P356B | Sodium Hypochlorite Pump 2 Chlorine tank | Input 4 | XV250B | Lime Water Intake Tank 2 (T210B) Open | Input 4 | XV303D | Lamella 4 Sludge Discharge (T303D) Closed | Input 4 |  |  | Input 4 | P356B | Sodium Hypochlorite Pump 2 Chlorine tank | Input 4 |  |  | Input 4 | P356B | Sodium Hypochlorite Pump 2 Chlorine tank | Input 4 |  |  | Input 4 | P356B | Sodium Hypochlorite Pump 2 Chlorine tank
|  |  | Input 5 | LSHH210B | Lime Tank 2 (T210B) | Input 5 | LS353B | Caustic Soda Tank 2 (T353B) | Input 5 | XV251B | Lime Selector Tank 2 (T210B) C losed | Input 5 | P203B | Lime Circulation Pump 2 | Input 5 | P204A | Sodium Hypochlorite Pump 1 Disinfection Tank | Input 5 | XV250C | Lime Water Intake Tank 3 (T210C) Open | Input 5 | XV305 | Tertiary Treatment Main Valve Closed | Input 5 |  |  | Input 5 | P301A | Effluent Transfer Pump 1 | Input 5 |  |  | Input 5 | P301A | Effluent Transfer Pump 1 | Input 5 |  |  | Input 5 | P301A | Effluent Transfer Pump 1
|  |  | Input 6 | LSH210B | Lime Tank 2 (T210B) | Input 6 | LSHH301 | Effluent Sump (T301) | Input 6 | XV251C | Lime Selector Tank 3 (T210C) C losed | Input 6 | P211A1 | Alum Pump 1 SBR #S1 | Input 6 | P204B | Sodium Hypochlorite Pump 2 Disinfection Tank | Input 6 | XV250A | Lime Water Intake Tank 1 (T210A) Closed | Input 6 | M303A | Floculator 1 (T303A) | Input 6 | P203A | Lime Circulation Pump 1 | Input 6 | P301B | Effluent Transfer Pump 2 | Input 6 | P203A | Lime Circulation Pump 1 | Input 6 | P301B | Effluent Transfer Pump 2 | Input 6 | P203A | Lime Circulation Pump 1 | Input 6 | P301B | Effluent Transfer Pump 2
|  |  | Input 7 | LSL210B | Lime Tank 2 (T210B) | Input 7 | LSH301 | Effluent Sump (T301) | Input 7 | OPAlum | Alum Selector Tank 1 (T351A) | Input 7 | P211A2 | Alum Pump 2 SBR #S1 | Input 7 |  |  | Input 7 | XV250B | Lime Water Intake Tank 2 (T210B) Closed | Input 7 | M303B | Floculator 2 (T303B) | Input 7 | P203B | Lime Circulation Pump 2 | Input 7 | P302A | Collection Pump 1 | Input 7 | P203B | Lime Circulation Pump 2 | Input 7 | P302A | Collection Pump 1 | Input 7 | P203B | Lime Circulation Pump 2 | Input 7 | P302A | Collection Pump 1
|  |  | Input 8 | LSLL210B | Lime Tank 2 (T210B) | Input 8 | LSL301 | Effluent Sump (T301) | Input 8 | OPAlum | Alum Selector Tank 2 (T351B) | Input 8 | P211B1 | Alum Pump 1 SBR #S2 | Input 8 |  |  | Input 8 | XV250C | Lime Water Intake Tank 3 (T210C) Closed | Input 8 | M303C | Floculator 3 (T303C) | Input 8 | P211A1 | Alum Pump 1 SBR #S1 | Input 8 | P302B | Collection Pump 2 | Input 8 | P211A1 | Alum Pump 1 SBR #S1 | Input 8 | P302B | Collection Pump 2 | Input 8 | P211A1 | Alum Pump 1 SBR #S1 | Input 8 | P302B | Collection Pump 2
|  |  | Input 9 | LSHH210C | Lime Tank 3 (T210C) | Input 9 | LSHH302 | Collection Sump (T302) | Input 9 | OPAlum | Alum Selector Tank 3 (T351C) | Input 9 | P211B2 | Alum Pump 2 SBR #S2 | Input 9 |  |  | Input 9 | XV303A | Lamella 1 Sludge Discharge (T303A) Open | Input 9 | M303D | Floculator 4 (T303D) | Input 9 | P211A2 | Alum Pump 2 SBR #S1 | Input 9 | K301A | Air Compressor 1 | Input 9 | P211A2 | Alum Pump 2 SBR #S1 | Input 9 | K301A | Air Compressor 1 | Input 9 | P211A2 | Alum Pump 2 SBR #S1 | Input 9 | K301A | Air Compressor 1
|  |  | Input 10 | LSH210C | Lime Tank 3 (T210C) | Input 10 | LSH302 | Collection Sump (T302) | Input 10 | OPAlum | Alum Selector Tank 4 (T351D) | Input 10 | P352A | Alum Pump 1 Tertiary Dosing | Input 10 |  |  | Input 10 | XV303B | Lamella 2 Sludge Discharge (T303B) Open | Input 10 | P301A | Effluent Transfer Pump 1 | Input 10 | P211B1 | Alum Pump 1 SBR #S2 | Input 10 | K301B | Air Compressor 2 | Input 10 | P211B1 | Alum Pump 1 SBR #S2 | Input 10 | K301B | Air Compressor 2 | Input 10 | P211B1 | Alum Pump 1 SBR #S2 | Input 10 | K301B | Air Compressor 2
|  |  | Input 11 | LSL210C | Lime Tank 3 (T210C) | Input 11 | LSL302 | Collection Sump (T302) | Input 11 | OPCaustic | Caustic Soda Selector Tank 1 (T353A) | Input 11 | P352B | Alum Pump 2 Tertiary Dosing | Input 11 |  |  | Input 11 | XV303C | Lamella 3 Sludge Discharge (T303C) Open | Input 11 | P301B | Effluent Transfer Pump 2 | Input 11 | P211B2 | Alum Pump 2 SBR #S2 | Input 11 |  |  | Input 11 | P211B2 | Alum Pump 2 SBR #S2 | Input 11 | M303A | Floculator 1 (T303A) | Input 11 | P211B2 | Alum Pump 2 SBR #S2 | Input 11
|  |  | Input 12 | LSLL210C | Lime Tank 3 (T210C) | Input 12 | LSH308A | Re-Use Water Storage Tank 1 HIGH (T308A) | Input 12 | OPCaustic | Caustic Soda Selector Tank 2 (T353B) | Input 12 | XV210A1 | Lime Valve 1 #S1 Open | Input 12 |  |  | Input 12 | XV303D | Lamella 4 Sludge Discharge (T303D) Open | Input 12 | P302A | Collection Pump 1 | Input 12 | P352A | Alum Pump 1 Tertiary Dosing | Input 12 |  |  | Input 12 | P352A | Alum Pump 1 Tertiary Dosing | Input 12 | M303B | Floculator 2 (T303B) | Input 12 | P352A | Alum Pump 1 Tertiary Dosing | Input 12
|  |  | Input 13 | LS351A | Alum Tank 1 (T351A) | Input 13 | LSH308B | Re-Use Water Storage Tank 2 HIGH (T308B) | Input 13 | OPSodium | Sodium Hypochlorite Selector Tank 1 (T355A) | Input 13 | XV201A2 | Lime Valve 3 #S2 Open | Input 13 |  |  | Input 13 | XV305 | Tertiary Treatment Main Valve Open | Input 13 | P302B | Collection Pump 2 | Input 13 | P352B | Alum Pump 2 Tertiary Dosing | Input 13 |  |  | Input 13 | P352B | Alum Pump 2 Tertiary Dosing | Input 13 | M303C | Floculator 3 (T303C) | Input 13 | P352B | Alum Pump 2 Tertiary Dosing | Input 13
|  |  | Input 14 | LS351B | Alum Tank 2 (T351B) | Input 14 |  |  | Input 14 | OPSodium | Sodium Hypochlorite Selector Tank 2 (T355B) | Input 14 | XV210A1 | Lime Valve 1 #S1 Closed | Input 14 |  |  | Input 14 |  |  | Input 14 | K301A | Air Compressor 1 | Input 14 | P354A | Caustic Soda Pump 1 | Input 14 |  |  | Input 14 | P354A | Caustic Soda Pump 1 | Input 14 | M303D | Floculator 4 (T303D) | Input 14 | P354A | Caustic Soda Pump 1 | Input 14
|  |  | Input 15 | LS351C | Alum Tank 3 (T351C) | Input 15 |  |  | Input 15 | OPSodium | Sodium Hypochlorite Selector Tank 3 (T355C) | Input 15 | XV201A2 | Lime Valve 3 #S2 Closed | Input 15 |  |  | Input 15 |  |  | Input 15 | K301B | Air Compressor 2 | Input 15 | P354B | Caustic Soda Pump 2 | Input 15 |  |  | Input 15 | P354B | Caustic Soda Pump 2 | Input 15 |  |  | Input 15 | P354B | Caustic Soda Pump 2 | Input 15
|  |  | Input 16 | LS351D | Alum Tank 4 (T351D) | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16
Legend |  |  | A2 EK1100 #1 |  |  | A18 EL2809 #1 |  |  | A19 EL2809 #2 |  |  | A20 EL2809 #3 |  |  | A21 EL2809 #4 |  |  | A22 EL2809 #5 |  |  | A23 EL2809 #6 |  |  | A24 EL3154 #1 |  |  | A25 EL3154 #2 |  |  | A26 EL3154 #3 |  |  | A27 EL9011 #2
| Coupler |  | Coupler |  | E-Bus | Digital Output Module |  | Open / Close & Start / Stop | Digital Output Module |  | Open / Close & Start / Stop | Digital Output Module |  | Open / Close & Start / Stop | Digital Output Module |  | AUXILARY LAMP | Digital Output Module |  | AUXILARY LAMP | Digital Output Module |  | AUXILARY LAMP | Analog Input Module |  | Entry | Analog Input Module |  | Discharge | Analog Input Module |  | Chlorinization | End Terminal
| Input |  |  |  |  | Input 1 | XV250A | Lime Water Intake Tank 1 (T210A) | Input 1 | P354A | Caustic Soda Pump 1 | Input 1 | XV303A | Lamella 1 Sludge Discharge (T303A) | Input 1 | AUX-1 | Circulation Overflow | Input 1 | AUX-17 | Lime1 in Service | Input 1 | AUX-33 | Lime1 LOW | Input 1 | FT300 | Effluent Flowrate Entry | Input 1 | FT301 | Treated Effluent Flowrate Discharge | Input 1 | CL303 | Residual Chlorine Analyzer
| Output |  |  |  |  | Input 2 | XV250B | Lime Water Intake Tank 2 (T210B) | Input 2 | P354B | Caustic Soda Pump 2 | Input 2 | XV303B | Lamella 2 Sludge Discharge (T303B) | Input 2 | AUX-2 | System Inlet Monitoring | Input 2 | AUX-18 | Lime2 in Service | Input 2 | AUX-34 | Lime2 LOW | Input 2 | AT300 | Effluent Turbidity Entry | Input 2 | AT302 | Treated Effluent Turbidity Discharge | Input 2 | CL304 | Final Chlorine Analyzer
| Analog |  |  |  |  | Input 3 | XV250C | Lime Water Intake Tank 3 (T210C) | Input 3 | P356A | Sodium Hypochlorite Pump 1 Chlorine tank | Input 3 | XV303C | Lamella 3 Sludge Discharge (T303C) | Input 3 | AUX-3 | System Outlet Monitoring | Input 3 | AUX-19 | Lime3 in Service | Input 3 | AUX-35 | Lime3 LOW | Input 3 | PHT301 | Effluent pH Level Entry | Input 3 | PHT303 | Treated Effluent pH Level Discharge | Input 3
| End Terminal |  |  |  |  | Input 4 | XV251A | Lime Selector Tank 1 (T210A) Open | Input 4 | P356B | Sodium Hypochlorite Pump 2 Chlorine tank | Input 4 | XV303D | Lamella 4 Sludge Discharge (T303D) | Input 4 | AUX-4 | Chlorine-HIGH | Input 4 | AUX-20 | Alum1 in Service | Input 4 | AUX-36 | Alum1 LOW | Input 4 |  |  | Input 4 |  |  | Input 4
[6 empty] | Input 5 | XV251B | Lime Selector Tank 2 (T210B) Open | Input 5 | P204A(Relay) | Sodium Hypochlorite Pump 1 Disinfection Tank | Input 5 | XV305 | Tertiary Treatment Main Valve | Input 5 | AUX-5 | SBR-Dosing | Input 5 | AUX-21 | Alum2 in Service | Input 5 | AUX-37 | Alum2 LOW
[6 empty] | Input 6 | XV251C | Lime Selector Tank 3 (T210C) Open | Input 6 | P204B(Relay) | Sodium Hypochlorite Pump 2 Disinfection Tank | Input 6 | M303A | Floculator 1 (T303A) | Input 6 | AUX-6 | Chlorine-Dosing | Input 6 | AUX-22 | Alum3 in Service | Input 6 | AUX-38 | Alum3 LOW
[6 empty] | Input 7 | XV251A | Lime Selector Tank 1 (T210A) Closed | Input 7 | P211A1 | Alum Pump 1 SBR #S1 | Input 7 | M303B | Floculator 2 (T303B) | Input 7 | AUX-7 | Disinfection-Dosing | Input 7 | AUX-23 | Alum4 in Service | Input 7 | AUX-39 | Alum4 LOW
[6 empty] | Input 8 | XV251B | Lime Selector Tank 2 (T210B) Closed | Input 8 | P211A2 | Alum Pump 2 SBR #S1 | Input 8 | M303C | Floculator 3 (T303C) | Input 8 | AUX-8 | Tertiary-Dosing | Input 8 | AUX-24 | Caustic1 in Service | Input 8 | AUX-40 | Caustic1 LOW
[6 empty] | Input 9 | XV251C | Lime Selector Tank 3 (T210C) Closed | Input 9 | P211B1 | Alum Pump 1 SBR #S2 | Input 9 | M303D | Floculator 4 (T303D) | Input 9 | AUX-9 | Power Status | Input 9 | AUX-25 | Caustic2 in Service | Input 9 | AUX-41 | Caustic2 LOW
[6 empty] | Input 10 | P210A1 | Lime Pump 1 #S1 | Input 10 | P211B2 | Alum Pump 2 SBR #S2 | Input 10 | P301A | Effluent Transfer Pump 1 | Input 10 | AUX-10 | Alarm Status | Input 10 | AUX-26 | Sodium1 in Service | Input 10 | AUX-42 | Sodium1 LOW
[6 empty] | Input 11 | P210A2 | Lime Pump 2 #S1 | Input 11 | P352A | Alum Pump 1 Tertiary Dosing | Input 11 | P301B | Effluent Transfer Pump 2 | Input 11 | AUX-11 |  | Input 11 | AUX-27 | Sodium2 in Service | Input 11 | AUX-43 | Sodium2 LOW
[6 empty] | Input 12 | P210A3 | Lime Pump 3 #S1 | Input 12 | P352B | Alum Pump 2 Tertiary Dosing | Input 12 | P302A | Collection Pump 1 | Input 12 | AUX-12 |  | Input 12 | AUX-28 | Sodium3 in Service | Input 12 | AUX-44 | Sodium3 LOW
[6 empty] | Input 13 | P210A1 | Lime Valve 1 #S2 Open | Input 13 | P203A | Lime Circulation Pump 1 | Input 13 | P302B | Collection Pump 2 | Input 13 | AUX-13 |  | Input 13 | AUX-29 |  | Input 13 | AUX-45
[6 empty] | Input 14 | P210A2 | Lime Valve 3 #S2 Open | Input 14 | P203B | Lime Circulation Pump 2 | Input 14 | K301A | Air Compressor 1 | Input 14 | AUX-14 |  | Input 14 | AUX-30 |  | Input 14 | AUX-46
[6 empty] | Input 15 | P210A1 | Lime Valve 1 #S2 Closed | Input 15 |  |  | Input 15 | K301B | Air Compressor 2 | Input 15 | AUX-15 |  | Input 15 | AUX-31 |  | Input 15 | AUX-47
[6 empty] | Input 16 | P210A2 | Lime Valve 3 #S2 Closed | Input 16 |  |  | Input 16 |  |  | Input 16 | AUX-16 |  | Input 16 | AUX-32 |  | Input 16 | AUX-48