## Interlock Table
Sludge Thickening and Storage System - Interlock Table
Stage | Equipment (Start/Stop)(Open/Closed) | Internal Interlock | Interlock Status | Interlock Execution | Interlock Safety Check | Additional Interlock Concern | Auxilary Lamp | New Requirement | Function | Justification | Manual Fall Back
Sludge Holding Tank | Level Sensor | Level Sensor LSHH 501 | HIGH Level | Desludge Pump Stop P201A/B |  | Sent GUI Alarm | Sent Auxilary - Sludge Overflow |  | Prevend overflow on Sludge Storage
Tertiary Sludge Discharge XV303A/B/C/D
|  | Level Sensor LSH 501 | OP Level | Sludge Feed Pump Start | Sludge Pit level not on HIGH |  |  |  | Signals Optimum level to start pump
Filtrate level not on HIGH
|  |  |  | Blower Operation Start |  |  |  |  | To make sure Sludge in Raw Condition
|  | Level Sensor LSL 501 | LOW Level | Sludge Feed Pump Stop |  | Sent GUI Alarm |  |  | To avoid dry running for Feed pump
|  |  |  | Blower Operation Stop |  |  |  |  | To make sure Sludge in Raw Condition | Utilization of power consumption
Feed Pump - | Sludge Feed Pump | Level Sensor LSH 501 | OP Level | Start Drum Belt | When Reach LOW Level,start only when reach OP level. |  |  |  | Signals Optimum level to start pump
|  | Sludge Pit Sensor | Not on HIGH Level
|  | Drum Belt | STOP | Sludge Feed Pump Stop
Drum Thickener System | Drum Belt | XV Backwash Valve | Open Valve | Start Backwash System | Check Reused Water not in Low Level
|  | Flocculator | Start
|  | Polymer Level LSH PU501 | Not in LOW level | Stop Thickener if LOW Level | Delay 10s after Thickener Start | Sent GUI Alarm | Sent Auxilary - Polymer LOW
|  | Sludge Pit Sensor | Not in High Level | When Reach HIGH Level,stop Thickener Process |  | Sent GUI Alarm | Sent Auxilary - Sludge Pit Overflow
Backwash Water System | Water Pump P505 | XV Backwash Valve | Open Valve | Start Water Pump P505
|  | Pressure Switch PSL 505 | below 7 bar | Stop Water Pump P505
| Level Sensor | LSL Reused Water | LOW Level | Stop Water Pump P505 |  |  | Sent Auxilary - Low level Reused Water
Sludge Pit | Level Sensor | Level Sensor LSH 600 | Analog Reading HIGH | Stop Feed Pump |  | Sent GUI Alarm | Sent Auxilary - Sludge Pit Overflow
|  | Level Sensor LSL 600 | Analog Reading LOW | Start Feed Pump | Check OtherRelated Level Sensor | Sent GUI Alarm
Polymer Preparation System | Level Sensor | LSH PU501 | Not in LOW level | Open XV Diagpharm
|  | LSL PU501 | LOW Level | Stop Thickener process |  | Sent GUI Alarm | Sent Auxilary - LowPolymer
| Valve | XV Polymer A/B | Open Valve |  | Closed if Low Level LSL PU501 |  | Sent Auxilary - LowPolymer
|  | XV Diagrpharm | Open Valve |  | Closed if Low Level LSL PU501 |  | Sent Auxilary - LowPolymer
Filtrate Sump | Level Sensor | LSH filtrate | HIGH | Filtrate Pump standby | SBR Transfer Start-then only Filtrate Pump Start | Sent GUI Alarm | Sent Auxilary - Filtrate Overflow
|  | LSL Filtrate | LOW | Stop Filtrate Pump

## PLC Assignment
Sludge Thickening and Storage System
A1 EK1501 #1 |  |  | A2 EL1809 #1 |  |  | A3 EL1809 #2 |  |  | A4 EL1809 #3 |  |  | A5 EL1809 #4 |  |  | A6 EL1809 #5 |  |  | A9 EL1809 #6 |  |  | A10 EL1809 #7 |  |  | A11 EL1809 #8 |  |  | A11 EL1809 #9 |  |  | A12 EL 3054 #1 |  |  | A13 EL2809 #1 |  |  | A14 EL2809 #2 |  |  | A15 EL2809 #3 |  |  | A16 EL9011 #1
Coupler |  | Fiber | Digital Input Module |  | Level Sensor | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Open / Close & Start / Stop Status | Digital Input Module |  | Trip Status | Digital Input Module |  | Trip Status | Digital Input Module |  | Local /Remote Status | Digital Input Module |  | Emergency Stop | Digital Input Module |  | Odour ( On / Off Status )/Overload | Digital Input Module |  | Odour Overload/E-stop | Analog Module |  |  | Digital Output Module |  | Open / Close & Start / Stop | Digital Output Module |  | Open / Close & Start / Stop | Digital Output Module |  |  | End Terminal
|  |  | Input 1 | TBA | Fan Status | Input 1 | P501A | Sludge Feed Pump 1 | Input 1 | D503A | Drum Thickener 1 | Input 1 | B501A | Blower 1 Overload | Input 1 | M502A | Floculator 1 Overload | Input 1 | P501A | Sludge Feed Pump 1 | Input 1 | P501A | Sludge Feed Pump 1 | Input 1 | VE801A | Suction Fan | Input 1 | P806A1 | NAOH Pump 1 Overload | Input 1 | LSH 600 | Sludge Pit Sensor | Input 1 | XV PU502 | Diagpharm Air Valve 1 | Input 1 | B501A | Blower 1 | Input 1 | AUX510 | SludgeStorage HiGH
|  |  | Input 2 | TBA | Door Panel | Input 2 | P501B | Sludge Feed Pump 2 | Input 2 | D503B | Drum Thickener 2 | Input 2 | B501A | Blower 1 Incomplete | Input 2 | M502B | Floculator 2 Overload | Input 2 | P501B | Sludge Feed Pump 2 | Input 2 | P501B | Sludge Feed Pump 2 | Input 2 | P802A | Circulation Pump 1 | Input 2 | P806A2 | NAOH Pump 2 Overload | Input 2 |  |  | Input 2 | M502A | Floculator 1 | Input 2 | B501B | Blower 2 | Input 2 | AUX511 | Reuse Water Storage Low
|  |  | Input 3 | LSH501A | Sludge Storage 1 | Input 3 | P501C | Sludge Feed Pump 3 | Input 3 | P505A | Backwash Water Pump 1 | Input 3 | B501B | Blower 2 Overload | Input 3 | D503A | Drum Thickener 1 Overload | Input 3 | P501C | Sludge Feed Pump 3 | Input 3 | P501C | Sludge Feed Pump 3 | Input 3 | P803A | Circulation Pump 2 | Input 3 | P807A1 | NAOCL Pump 1 Overload | Input 3 |  |  | Input 3 | M502B | Floculator 2 | Input 3 | B501C | Blower 3 | Input 3 | AUX512 | Filtrate Sump HiGH
|  |  | Input 4 | LSHH501A | Sludge Storage 1 | Input 4 | B501A | Blower 1 | Input 4 | P505B | Backwash Water Pump 2 | Input 4 | B501B | Blower 2 Incomplete | Input 4 | D503B | Drum Thickener 2 Overload | Input 4 | B501A | Blower 1 | Input 4 | B501A | Blower 1 | Input 4 | P804A | Circulation Pump 3 | Input 4 | P807A2 | NAOCL Pump 2 Overload | Input 4 |  |  | Input 4 | M503A | Drum Thickener 1 | Input 4 | P501A | Sludge Feed Pump 1 | Input 4 | AUX513 | Sludge Pit HiGH
|  |  | Input 5 | LSL501A | Sludge Storage 1 | Input 5 | B501B | Blower 2 | Input 5 | P505C | Backwash Water Pump 3 | Input 5 | B501C | Blower 3 Overload | Input 5 | P505A | Backwash Water Pump 1 Overload | Input 5 | B501B | Blower 2 | Input 5 | B501B | Blower 2 | Input 5 | P805A1 | H2S04 Pump 1 | Input 5 | VE801A | Suction Fan E-Stop |  |  |  | Input 5 | M503B | Drum Thickener 2 | Input 5 | P501B | Sludge Feed Pump 2 | Input 5 | AUX514 | Polymer Level Low
|  |  | Input 6 | LSH501B | Sludge Storage 2 | Input 6 | B501C | Blower 3 | Input 6 | XV501A | Air Blower Valve Open A | Input 6 | B501C | Blower 3 Incomplete | Input 6 | P505A | Backwash Water Pump 1 Incomplete | Input 6 | B501C | Blower 3 | Input 6 | B501C | Blower 3 | Input 6 | P805A2 | H2S04 Pump 2 | Input 6 | P802A | Circulation Pump 1 E-Stop |  |  |  | Input 6 | M502A | Floculator Valve 1 | Input 6 | P501C | Sludge Feed Pump 3 | Input 6 | AUX515 | Alarm Event
|  |  | Input 7 | LSHH501B | Sludge Storage 2 | Input 7 | M502A | Floculator 1 | Input 7 | XV501A | Air Blower Valve Closed A | Input 7 | P501A | Sludge Feed Pump 1 Overload | Input 7 | P505B | Backwash Water Pump 2 Overload | Input 7 | M502A | Floculator 1 | Input 7 | M502A | Floculator 1 | Input 7 | P806A1 | NAOH Pump 1 | Input 7 | P803A | Circulation Pump 2 E-Stop |  |  |  | Input 7 | M502B | Floculator Valve 2 | Input 7 | P505A | Backwash Water Pump 1 | Input 7 | AUX516 | Power Status
|  |  | Input 8 | LSL501B | Sludge Storage 2 | Input 8 | M502B | Floculator 2 | Input 8 | XV501B | Air Blower Valve Open B | Input 8 | P501A | Sludge Feed Pump 1 Incomplete | Input 8 | P505B | Backwash Water Pump 2 Incomplete | Input 8 | M502B | Floculator 2 | Input 8 | M502B | Floculator 2 | Input 8 | P806A2 | NAOH Pump 2 | Input 8 | P804A | Circulation Pump 3 E-Stop |  |  |  | Input 8 | P602A | Filtrate Pump 1 | Input 8 | P505B | Backwash Water Pump 2
|  |  | Input 9 | LSH 620 | Filtrate Sump Level | Input 9 | P602A | Filtrate Pump 1 | Input 9 | XV501B | Air Blower Valve Closed B | Input 9 | P501B | Sludge Feed Pump 2 Overload | Input 9 | P505C | Backwash Water Pump 3 Overload | Input 9 | D503A | Drum Thickener 1 | Input 9 | D503A | Drum Thickener 1 | Input 9 | P807A1 | NAOCL Pump 1 | Input 9 | P805A1 | H2S04 Pump 1 E-Stop |  |  |  | Input 9 | P602B | Filtrate Pump 2 | Input 9 | P505C | Backwash Water Pump 3
|  |  | Input 10 | LSL620 | Filtrate Sump Level | Input 10 | P602B | Filtrate Pump 2 | Input 10 | XV PU501A | Polymer Valve 1 Open | Input 10 | P501B | Sludge Feed Pump 2 Incomplete | Input 10 | P505C | Backwash Water Pump 3 Incomplete | Input 10 | D503B | Drum Thickener 2 | Input 10 | D503B | Drum Thickener 2 | Input 10 | P807A2 | NAOCL Pump 2 | Input 10 | P805A2 | H2S04 Pump 2 E-Stop |  |  |  | Input 10 | XV PU501A | Polymer Valve 1 Open | Input 10 | XV501A | Air Blower Valve Open A
|  |  | Input 11 | LSL PU501 | Polymer Tank Level | Input 11 | XV 505A | Solenoid Valve Line 1 Open | Input 11 | XV PU501A | Polymer Valve 2 Closed | Input 11 | P501C | Sludge Feed Pump 3 Overload | Input 11 | M503 | Polymer Stirrer Overload | Input 11 | P505A | Backwash Water Pump 1 | Input 11 | P505A | Backwash Water Pump 1 | Input 11 | VE801A | Suction Fan Overload | Input 11 | P806A1 | NAOH Pump 1 E-Stop |  |  |  | Input 11 | XV PU501A | Polymer Valve 2 Closed | Input 11 | XV501B | Air Blower Valve Open B
|  |  | Input 12 | LSH PU501 | Polymer Tank Level | Input 12 | XV 505B | Solenoid Valve Line 2 Open | Input 12 | XV PU501B | Polymer Valve 2 Open | Input 12 | P501C | Sludge Feed Pump 3 Incomplete | Input 12 |  |  | Input 12 | P505B | Backwash Water Pump 2 | Input 12 | P505B | Backwash Water Pump 2 | Input 12 | P802A | Circulation Pump 1 Overload | Input 12 | P806A2 | NAOH Pump 2 E-Stop |  |  |  | Input 12 | XV PU501B | Polymer Valve 2 Open | Input 12 | XV501A | Air Blower Valve Closed A
|  |  | Input 13 | PSL 505 A | Pressure SW Water Line1 | Input 13 | XV PU502 | Diagpharm Air Valve 1 Open | Input 13 | XV PU501B | Polymer Valve 1 Closed | Input 13 | P602A | Filtrate Pump 1 | Input 13 |  |  | Input 13 | P505C | Backwash Water Pump 3 | Input 13 | P505C | Backwash Water Pump 3 | Input 13 | P803A | Circulation Pump 2 Overload | Input 13 | P807A1 | NAOCL Pump 1 E-Stop |  |  |  | Input 13 | XV PU501B | Polymer Valve 1 Closed | Input 13 | XV501B | Air Blower Valve Closed B
|  |  | Input 14 | PSL 505 B | Pressure SW Water Line2 | Input 14 | XV 505A | Solenoid Valve Line 1 Closed | Input 14 | M 503 | Polymer Stirrer Run | Input 14 | P602B | Filtrate Pump 2 | Input 14 |  |  | Input 14 | P602A | Filtrate Pump 1 | Input 14 | P602A | Filtrate Pump 1 | Input 14 | P804A | Circulation Pump 3 Overload | Input 14 | P807A2 | NAOCL Pump 2 E-Stop |  |  |  | Input 14 | XV 505A | Solenoid Valve Line 1 | Input 14 | M 503 | Polymer Stirrer Forward
|  |  | Input 15 |  |  | Input 15 | XV 505B | Solenoid Valve Line 2 Closed | Input 15 |  |  | Input 15 |  |  | Input 15 |  |  | Input 15 | P602B | Filtrate Pump 2 | Input 15 | P602B | Filtrate Pump 2 | Input 15 | P805A1 | H2S04 Pump 1 Overload | Input 15 | [5 empty] | Input 15 | XV 505B | Solenoid Valve Line 2 | Input 15 | M 503 | Polymer Stirrer Reverse
|  |  | Input 16 |  |  | Input 16 | XV PU502 | Diagpharm Air Valve 1 Closed | Input 16 |  |  | Input 16 |  |  | Input 16 |  |  | Input 16 | M503 | Polymer Stirrer | Input 16 | M503 | Polymer Stirrer | Input 16 | P805A2 | H2S04 Pump 2 Overload | Input 16 | [5 empty] | Input 16 |  |  | Input 16 | XV PU502 | Diagpharm Air Valve 1
Legend
Coupler
Input
Output
Analog
End Terminal