## Interlock Table
Reused Water System - Interlock Table
Stage | Equipment (Start/Stop)(Open/Closed) | Internal Interlock | Interlock Status | Interlock Execution | Interlock Safety Check | Additional Interlock Concern | Auxilary Lamp | New Requirement | Function | Justification | Manual Fall Back
Priming System | Vacuum Pump | Flow Activation Switch FSL 101 | Trigger | Vacuum Pump Start |  |  |  |  | to sense the existence of water for Priming system and act as safety cut off for vacuum pump
|  |  | Not Trigger |  | Vacuum Pump Stop
|  | Solenoid Valve XV401 | Open |  |  | Closed after System Primed |  |  | Open potable water access for priming purpose
|  | Vacuum Chest LSH405 | HIGH Level |  |  | Standby Recycle Pump | Sent Auxilary - System Primed |  | To make sure System is Primed for safely run the pumps operation
|  |  | LOW Level |  | Recycle Pump Stop | Sent GUI Alarm |  |  | To avoid dry running for recycle pump
|  | Digital Pressure Gauge | minus Pressure | Start Vacuum Pump |  | Check Vacuum Chest Sensor LSH 405 |  | Yes | To maintain system pressure and make sure system is on prime condition at all time | Existing Design start and stop the vacuum pump manually.
|  |  | positive Pressure | Stop Vacuum Pump
|  | Jockey Pump | Stop | [6 empty] | To prevent pumps Run on dry condition
|  | Lead Pump | Stop | [6 empty] | To prevent pumps Run on dry condition
Pumping Sequence - Normal Operation | Jockey Pump /1st Lead Pump | Level Sensor LSH 309 | OP Level |  | not in LOW Level |  |  |  | Signals Optimum level to start pump
|  | PSL 411 | 6 - 8 Bar | Jockey Pump Start/ 1st Lead Pump Stop | Primed Status must be Satisfied/vacuum pump stop | Jockey Pump Stop at 8 Bar
|  | PSL 411 | 5.2 - 6.4 Bar | Jockey Pump Start/ 1st Lead Pump Start | Primed Status must be Satisfied/vacuum pump stop
Pumping Sequence - Water Boosting | Jockey Pump/ 1st Lead Pump/ 2nd Lead Pump | Level Sensor LSH 309 | OP Level |  | not in LOW Level |  | Sent Auxilary- Low Pressure |  | Signals Optimum level to start pump
|  | PSL 411 | 4.7 - 5.9 Bar | Jockey Pump Start/ 1st Lead Pump Start/2nd Lead Pump Start | Primed Status must be Satisfied/vacuum pump stop
|  | PSL 411 | < 3.5 Bar | Delay 10s if still below 3.5 Bar- ALL stop
Separate Pressure Switch | PSL 411 | Control Pump Schedule | Analog 0-10 Bar Operation |  |  | Maintain System Pressure at 8 Bar |  |  | Sense cut in/out of pump operation
|  | <3.5 Bar | Analog reading | Delay 10s if still below 3.5 Bar- ALL stop | Delay 10s if still below 3.5 Bar- ALL stop | Sent GUI Alarm | Sent Auxilary- Low Pressure |  | Line Break Protection
| PSL 412 | >8.2 Bar | Trigger | Stop ALL pump | Stop ALL pump | Sent GUI Alarm | Sent Auxilary - Alarm |  | Choke Protection
Water Storage | Level Sensor LSH 309A | LSH 309A | Low Level | Stop Recycle Pump/Start Tertiary Pump |  | Sent GUI Alarm |  |  |  | To avoid dry running
| Level Sensor LSH 309B | LSH 309B | Low Level | Stop Recycle Pump/Start Tertiary Pump |  | Sent GUI Alarm |  |  |  | To avoid dry running

## PLC Assignment
Re-Use Water Pump- PLC Assignment
A1 EK1501 |  | A2 EL 1809 #1 |  |  | A3 EL 1809 #2 |  |  | A4 EL 1809 #3 |  |  | A5 EL 1809 #4 |  |  | A6 EL 2809 #1 |  |  | A7 EL 3054 #1 |  |  | A8 EL9011 #1
Coupler | Fiber | Input Module |  | Status |  | Input Module | (Trip) | Input Module |  | (Local / Remote) / (Off / On Status) | Input Module |  | Emergency Stop | Output Module |  | Start/Stop/Open/Closed | Output Module |  | Analog reading | End Terminal
|  | Input 1 | LSH309A | Water Level Low Tank 1 | Input 1 | P401A | Lead Pump Overload | Input 1 | P401A | Lead Pump Local / Remote | Input 1 | P401A | Lead Pump | Input 1 | XV401 | Solenoid Valve | Input 1 | PSL411 | Pressure Transmitter
|  | Input 2 | LSH309B | Water Level Low Tank 2 | Input 2 | P401A | Lead Pump Incomplete | Input 2 | P401B | Lead Pump Local / Remote | Input 2 | P401B | Lead Pump | Input 2 | P401A | Lead Pump 1 | Input 2 | Spare
|  | Input 3 | LSH405 | Vacuum Chest High Level | Input 3 | P401B | Lead Pump Overload | Input 3 | P401C | Lead Pump Local / Remote | Input 3 | P401C | Lead Pump | Input 3 | P401B | Lead Pump 2 | Input 3 | Spare
|  | Input 4 | TMT07 | Fan Status | Input 4 | P401B | Lead Pump Incomplete | Input 4 | P401D | Lead Pump Local / Remote | Input 4 | P401D | Lead Pump | Input 4 | P401C | Lead Pump 3 | Input 4 | Spare
|  | Input 5 | DP07 | Door Panel | Input 5 | P401C | Lead Pump Overload | Input 5 | P402A | Jockey Pump Local / Remote | Input 5 | P402A | Jockey Pump | Input 5 | P401D | Lead Pump 4
|  | Input 6 | FSL101 | Fresh Water Activation | Input 6 | P401C | Lead Pump Incomplete | Input 6 | P402B | Jockey Pump Local / Remote | Input 6 | P402B | Jockey Pump | Input 6 | P402A | Jockey Pump 1
|  | Input 7 | PSL412 | Pressure Switch | Input 7 | P401D | Lead Pump Overload | Input 7 | P403A | Vacum Pump Local / Remote | Input 7 | P403A | Vacuum Pump | Input 7 | P402B | Jockey Pump 2
|  | Input 8 | PG413 | Minus Pressure Gauge | Input 8 | P401D | Lead Pump Incomplete | Input 8 | P403B | Vacum Pump Local / Remote | Input 8 | P403B | Vacuum Pump | Input 8 | P403A | Vacuum Pump 1
|  | Input 9 | PG414 | Positive Pressure Gauge | Input 9 | P402A | Jockey Pump Overload | Input 9 | P401A | Lead Pump On / Off Status | Input 9 | Spare |  | Input 9 | P403B | Vacuum Pump 2
|  | Input 10 | XV 401 | Solenoid Valve Open | Input 10 | P402A | Jockey Pump Incomplete | Input 10 | P401B | Lead Pump On / Off Status | Input 10 | Spare |  | Input 10 | AUX415 | Auxilary Lamp- Low Pressure
|  | Input 11 | XV 401 | Solenoid Valve Closed | Input 11 | P402B | Jockey Pump Overload | Input 11 | P401C | Lead Pump On / Off Status | Input 11 | Spare |  | Input 11 | AUX416 | Auxilary Lamp- Tank High Level
|  | Input 12 | Spare |  | Input 12 | P402B | Jockey Pump Incomplete | Input 12 | P401D | Lead Pump On / Off Status | Input 12 | Spare |  | Input 12 | AUX417 | Auxilary Lamp-System Primed
|  | Input 13 | Spare |  | Input 13 | P403A | Vacum Pump Overload | Input 13 | P402A | Jockey Pump On / Off Status | Input 13 | Spare |  | Input 13 | AUX418 | Auxilary Lamp- Alarm Event
|  | Input 14 | Spare |  | Input 14 | P403A | Vacum Pump Incomplete | Input 14 | P402B | Jockey Pump On / Off Status | Input 14 | Spare |  | Input 14 | AUX419 | Auxilary Lamp- Power Status
|  | Input 15 | Spare |  | Input 15 | P403B | Vacum Pump Overload | Input 15 | P403A | Vacum Pump On / Off Status | Input 15 | Spare |  | Input 15 | Spare
|  | Input 16 | Spare |  | Input 16 | P403B | Vacum Pump Incomplete | Input 16 | P403B | Vacum Pump On / Off Status | Input 16 | Spare |  | Input 16 | Spare